## Slide 1: Beacon 110
Single Channel Wall Mount Controller

## Slide 2: Internal Components
Optional Strobe
Alarm 3 LEDs
Alarm 1
Alarm 2
Fail
PCB Control Switches
UP/YES
DOWN/NO
ENTER
On/Off toggle switch
94 dB Buzzer Alarm
Alarm Reset Switch
Backlit LCD Display
Simultaneous readout of the gas type and concentration
Compact NEMA-4X weather resistant enclosure
Accepts any 4-20 mA transmitter or direct connect sensors for LEL / O2 / H2S / CO / CO2
2 programmable alarm levels per channel

## Slide 3: Calibration
Internal amp setup
  Sensor wired directly to controller.
  Gas applied directly to sensor.
  Adjustments made at controller.

## Slide 4: Calibration Mode
Press and hold the UP/YES Button to enter the calibration mode menu.
Press the YES button to proceed.

## Slide 5: Fresh Air Adjustment
Confirm that atmosphere is fresh before making fresh air adjustment.
Apply Zero Air to sensor if atmosphere is suspect.

## Slide 6: Fresh Air Adjustment
Allow sensor to stabilize when supplying Zero Air.

## Slide 7: Fresh Air Adjustment
Press the ENTER button when reading has stabilized and to complete the fresh air adjustment.

## Slide 8: Fresh Air Adjustment
If Fresh Air adjustment is successful, PASS will be displayed. If not, FAIL will be displayed.
Check sensor and test gas.

## Slide 9: Fresh Air Adjustment
The new fresh air setting will be saved in memory.

## Slide 10: Gas Adjustment
Upon completion of Air Adjustment, the Beacon 110 will prompt you if you would like to SPAN with Gas.
Press YES to continue.

## Slide 11: Gas Adjustment
Assemble calibration kit.
Attach calibration cup to sensor.

## Slide 12: Gas Adjustment
Apply Span gas to detector.

## Slide 13: Gas Adjustment
Allow reading to stabilize.
Maximum of two minutes.

## Slide 14: Gas Adjustment
Using UP or DOWN button, adjust span to proper setting then press the ENTER button to complete.

## Slide 15: Gas Adjustment
PASS will be displayed if calibration is successful.

## Slide 16: Gas Adjustment
Calibration data will be saved.

## Slide 17: Gas Adjustment
When calibration is complete, it will leave the calibration mode allowing time for the sensor to return to normal condition.

## Slide 18: Gas Adjustment
If the Beacon 110 is set up with a remote amp transmitter, “CAL AT AMP” will be displayed.

## Slide 19: Gas Adjustment
Calibrate detector as needed.
DMM, small flat blade screwdriver and calibration kit are required.

## Slide 20: Select Input Mode
Press and hold the UP/YES and DOWN/NO buttons to enter the Select Input mode.
This allows selection of the proper input type such as:
  O2 DIR
  TOX DIR
  LEL DIR
  4-20 mA transmitter

## Slide 21: Configuration Mode
Press and hold the UP/Yes and ENTER buttons to enter the Config Mode.
This mode is used for setting all internal parameters.

## Slide 22: Cal 4-20mA Mode
Press and hold the UP/YES, DOWN/NO and ENTER buttons to enter the Cal 4-20 Mode.
This mode is used for fine tuning the 4-20 mA output.

## Slide 23: Input Voltage and Firmware
Push and hold the DOWN/NO button to view the input voltage and firmware version.

## Slide 24: Terminal Connections
Form C contacts for Alarm-1, Alarm-2, and Fail relays.
  Common, Normally Open and Normally Closed contacts
  Note: Fail Relay is normally energized in normal operation, de-energized in fail condition.

## Slide 25: Questions?