## Slide 1: Beacon 200
2 Channel Wall Mount
Gas Detection Controller

## Slide 2: Internal Components
PCB Control Switches
ESCAPE
UP/YES
DOWN/NO
ENTER
Alarm LEDs
Alarm 1, yellow
Alarm 2, orange
Alarm 3, red
Fail, yellow
On/Off toggle switch
94 dB Buzzer Alarm
Alarm Reset Switch
Backlit LCD Display
2 Channels Displayed Simultaneously
NEMA-4X weather resistant enclosure
Accepts any 4-20 mA transmitter
2 programmable alarm levels per channel

## Slide 3: Alarm Indications
Condition | Cause | Visual Indications | Audible Indications
Alarm 1 | Increasing (decreasing for O2) gas reading at or above the alarm 1 set point | Alarm 1 LED on Gas reading alternates with Alarm-1 message Strobe (if installed) activates | Pulsing tone
Alarm 2 | Increasing gas reading at or above the alarm 2 set point | Alarm 2 LED is on Gas readings alternates with ALARM-2 message Strobe (if installed) activates | Pulsing tone
Fail | Disconnected or misconnected detector head wiring Display reading at -10% of full scale or lower Defective component | Fail LED is on Fail message replaces gas reading Strobe (if installed) activates | Steady tone
Low Power | No AC power and DC power source (primary or backup) less than 21.5 volts. | Fail LED is on SUPPLY VOLTAGE IS TOO LOW LOW POWER STANDBY message and actual voltage of incoming DC power | None

## Slide 4: Control & Setup Mode
Press and hold the ESCAPE and ENTER buttons to enter the Control & Setup Mode
This mode is used to set up all channel parameters

## Slide 5: Calibration Program
Press and hold the UP/YES and ENTER buttons to enter the Calibration Program.
Press the ENTER button to enter into this menu.
Note: Process describes direct connect sensor.

## Slide 6: Calibration Program
Setting the Calibration Timeout.
  Using the UP or DOWN buttons, set delay from 5 to 240 minutes.
Relays, audible and visual alarms are disabled during the Cal Timeout period.

## Slide 7: Calibration Program
Calibrate channel 1
Press the YES button to continue to next screen.
Note: If more than one channel is used, you can select channel 1, 2 or both.

## Slide 8: Calibration Program
Expose sensor to fresh air.
Use Zero air if needed.

## Slide 9: Calibration Program
Press the ENTER button to set FRESH AIR reading.

## Slide 10: Calibration Program
FRESH AIR set.

## Slide 11: Calibration Program
Press the YES button to continue calibration process.

## Slide 12: Calibration Program
Setting Span for Channel 1
  Using the UP or DOWN buttons, adjust SPAN Gas value to match concentration in the calibration gas cylinder.

## Slide 13: Calibration Program
Expose Calibration gas to sensor.
Allow reading to stabilize or a maximum of 2 minutes.

## Slide 14: Calibration Program
Reading with calibration gas applied.

## Slide 15: Calibration Program
When reading is stable press the ENTER button to set span.

## Slide 16: Calibration Program
Calibration Passed.

## Slide 17: Calibration Program
If you have a second sensor installed the Beacon 200 will prompt you if you want to Calibrate Channel 2.

## Slide 18: Calibration Program
For external amp transmitters, all calibrations are done at the detector head.

## Slide 19: Select Input Mode
With the Beacon 200 off, press and hold the ENTER button, then while pressing the ENTER button, power up the Beacon 200.
This allows selection of the proper input type such as:
  O2 DIR
  TOX DIR
  LEL DIR
  4-20 mA transmitter