## Slide 1: Beacon 3200
32 Channel Wall Mount Gas Detection Controller

## Slide 2
Table of Contents
Interior Detail – Slide 3-4
Alarm Indications – Slide 5-6
Start Up – Slide 7-9
Bar Graph View – Slide 10-11
History Graph View – Slide 12
Adjusting System Settings – Slide 13-15
Viewing Instrument Status – Slide 16-18
Changing Channel Settings – Slide 19-28
Setting Up Modbus Channels – Slide 29-40
Changing the Gas/Range Input Settings – Slide 41-47
Changing the Alarm Settings – Slide 48-52
Changing the Location – Slide 53-56
Creating Custom Ranges/ Gases/Units – Slide 57-61
Assigning Main Relays – Slide 62-66
Assigning Card Relays – Slide 67-71
Calibration Mode (Fresh Air) – Slide 72-79
Calibration Mode (Gas Adjust) – Slide 81-83
Viewing Min/Max Spans – Slide 84-87
Setting the Timeout – Slide 88-91
Changing the Install/Cal Dates – Slide 92-96
Maintenance (Alarm Test) – Slide 97-107
Sensor Logs Program – Slide 108-111
Parts List – Slide 112

## Slide 3
Interior Detail

## Slide 5
Condition | Cause | Visual Indications | Audible Indications
Alarm 1 | Increasing (decreasing for O2) gas reading at or above the alarm 1 set point | In list view, the status column displays Alarm 1 and background flashes yellow In Bar Graph view, the graph increments turn yellow If installed and set to activate for Alarm 1, strobe flashes | Pulsing Tone
Alarm 2 | Increasing (decreasing for O2) gas reading at or above the Alarm 2 set point | In List view, the Status column displays Alarm 1 / Alarm 2 and background flashes orange In Bar Graph view, the graph increments turn orange If installed, strobe continues to flash if set to activate for Alarm 1. If set to activate for Alarm 2 only or if channel in alarm is an oxygen channel, it begins to flash when an Alarm 2 condition begins | Pulsing Tone
Alarm 3 | Increasing gas reading at or above the Alarm 3 setpoint | In List view, the Status columns Displays Alarm 1 / Alarm 2 / Alarm 3 and background flashes red In Bar Graph view, the graph increments turn red If installed, strobe continues to flash if set to activate for Alarm 1 and/or Alarm 2 for non oxygen type channels or Alarm 1 for oxygen channels. If set to activate for Alarm 3 only, it begins to flash when an Alarm 3 condition begins | Pulsing Tone
Alarm Indications

## Slide 6
Alarm Indications (cont’d)
Condition | Cause | Visual Indications | Audible Indications
Fail | Disconnected or misconnected detector head wiring Display reading below -10% of full scale or lower Malfunctioning components | In list view, the Status column displays Fail and background flashes red In Bar Graph view, the graph increments turn red If installed and set to activate for fail, strobe flashes | Steady tone
Low Battery | No AC power and DC power source (primary or backup) less than 18.5 volts | Display shows Low Power Standby message and the input DC voltage | None

## Slide 7
Start Up
1. Complete the mounting and wiring procedures described earlier in this chapter.
2. Complete all installation procedures described in the detector head operator’s manual.
3. Verify that all wiring connections are correct and secure and that the Beacon 3200’s power
switch is in the OFF position.
4. Turn on power to any connected Modbus detector heads if power is not being supplied by the
Beacon 3200's Power Output Terminal Strip.
5. Plug in or turn on the incoming power source (AC or DC).
6. Turn on the power switch.
7. The warmup screen will display for 60 seconds. The warmup screen - shows the instrument’s firmware version.

## Slide 8
Start Up
If any Modbus detector heads are found, the Beacon 3200 asks if you want to import them.

## Slide 9
Start Up
When the warm-up period is complete, normal operation will begin. During normal operation,
the List display will indicate the target gas, current gas reading, channel status, and channel
location for each active channel.

## Slide 10
Bar Graph View
In Bar Graph view, the Beacon 3200 displays the channel number, the reading value, and a bar
graph depiction of the current gas reading.
Two Row Display

## Slide 11
Bar Graph View
One Row Display
The One Row/Two Rows button changes how many bar graphs are displayed at one time. This option is only available when there are more than 16 configured channels.
The Page Up and Page Down buttons scroll between the two pages. These buttons only appear in
Bar Graph view when there are more than 16 configured channels and the One Row display is
selected.

## Slide 12
History Graph Screen
The Beacon 3200 records data for each channel once per second and can store 7.5 years’ worth of
data. The History Graph screen shows the gas reading history for each channel, one channel at a
time.

## Slide 13
Adjusting System Settings
While in normal operation, press Setup.
If a password is enabled for Setup Mode, use the keypad to enter the password. The default password is 1234.
A pop-up message will indicate whether the relays remain active or deactivate upon entering Setup Mode. Press OK to proceed to Setup Mode.

## Slide 14
Adjusting System Settings (cont’d)
Press System Settings. Press the current parameter setting for the parameter you want to change.

## Slide 15
Adjusting System Settings (cont’d)
A menu appears that list the available settings.
Press the desired setting and press Enter.
Press Save Changes.

## Slide 16
Viewing Instrument Status
While in normal operation, press Setup.
If a password is enabled for Setup Mode, use the keypad to enter the password. The default password is 1234.
A pop-up message will indicate whether the relays remain active or deactivate upon entering Setup Mode. Press OK to proceed to Setup Mode.

## Slide 17
Viewing Instrument Status (cont’d)
Press Instrument Status

## Slide 18
Viewing Instrument Status (cont’d)
The Instrument Status screen displays the following information:
Version: This is the firmware version installed in the instrument.
Serial Number: This is the instrument serial number. It is entered at the factory and
cannot be changed in the field.
MAC Address: This is the instrument's MAC (Media Access Control) address and is a unique number specific to the instrument.
IPv4 Address: This is the IP address being used for the Ethernet connection.
Subnet Mask: This is the subnet mask being used for the Ethernet connection.
Gateway: This is the gateway being used for the Ethernet connection. DC voltage: This is the DC voltage running the instrument. If the unit is running from
AC, it is nominally the output of the AC/DC power supply.

## Slide 19
Changing Channel Settings
While in normal operation, press Setup.
If a password is enabled for Setup Mode, use the keypad to enter the password. The default password is 1234.
A pop-up message will indicate whether the relays remain active or deactivate upon entering Setup Mode. Press OK to proceed to Setup Mode.

## Slide 20
Changing Channel Settings (cont’d)
Press Channel Settings

## Slide 21
Changing Channel Settings (cont’d)
Press the channel number(s) of the channel(s) you would like to set up using the Channel Wizard
Note: Channels with an "s" next to the channel number are associated with installed sensor modules. Channels with an "m" next to the channel number are associated with a module slot position that does not have a sensor module installed and may be setup as a Modbus channel.

## Slide 22
Changing Channel Settings (cont’d)
Press Change State.

## Slide 23
Changing Channel Settings (cont’d)
Select Setup and press Enter.

## Slide 24
Changing Channel Settings (cont’d)
Select an input and press Next.

## Slide 25
Changing Channel Settings (cont’d)
Select a gas/range combination and press Next.

## Slide 26
Changing Channel Settings (cont’d)
Select the units and press Next. If the desired units are not listed, press Custom, type in the units, and press Enter. This parameter has a 6-character limit.
Note: If you do not see your gas/range combination listed, perform the following steps:
a. Click Custom + at the bottom of the screen.
b. If the desired gas name is not listed, press Custom, type in a gas name, and press Enter.
This parameter has a 20-character limit. Press Next when finished.

## Slide 27
Changing Channel Settings (cont’d)
Type in the range and press Next.

## Slide 28
Changing Channel Settings (cont’d)
Press OK to acknowledge pop up message.
Press Finish to save the new channel settings.

## Slide 29
Setting Up Modbus Channels
While in normal operation, press Setup.
If a password is enabled for Setup Mode, use the keypad to enter the password. The default password is 1234.
A pop-up message will indicate whether the relays remain active or deactivate upon entering Setup Mode. Press OK to proceed to Setup Mode.
This method is REQUIRED for connecting VOC and T3A detectors

## Slide 30
Setting Up Modbus Channels (cont’d)
Press Channel Settings.

## Slide 31
Setting Up Modbus Channels (cont’d)
Press the channel number(s) of the channel(s) you would like to set up using the Channel Wizard.

## Slide 32
Setting Up Modbus Channels (cont’d)
Press Change State.

## Slide 33
Setting Up Modbus Channels (cont’d)
Select Setup and press Enter.

## Slide 34
Setting Up Modbus Channels (cont’d)
Select an input and press Next.

## Slide 35
Setting Up Modbus Channels (cont’d)
Select a gas/range combination and press Next. The available options depends on the Input that was selected in the previous step.

## Slide 36
Setting Up Modbus Channels (cont’d)
IF you do not see your gas/range combination listed, perform the following steps:
  Click Custom +
  If the desired gas name is not listed, press Custom, type in a gas name, and press Enter. This parameter has a 20-character limit. Press Next when finished.

## Slide 37
Setting Up Modbus Channels (cont’d)
Type in the range & press Next.

## Slide 38
Setting Up Modbus Channels (cont’d)
A message will pop up to inform you that you can press Finish at any time to complete the installation.
Press OK to clear the message.
Press Finish to save the new channel settings.

## Slide 39
Setting Up Modbus Channels (cont’d)
While in the Channel Setting’s menu, press the newly setup channel’s Modbus Address.

## Slide 40
Setting Up Modbus Channels (cont’d)
A number pad appears. Type in the unused Modbus address. This Modbus address must match the Modbus address of the channel’s detector.
Press Enter to save the parameter.

## Slide 41
Changing the Gas/Range Input Settings
While in normal operation, press Setup.
If a password is enabled for Setup Mode, use the keypad to enter the password. The default password is 1234.
A pop-up message will indicate whether the relays remain active or deactivate upon entering Setup Mode. Press OK to proceed to Setup Mode.

## Slide 42
Changing the Gas/Range Input Settings (cont’d)
Press Channel Settings.

## Slide 43
Changing the Gas/Range Input Settings (cont’d)
Press the gas/range for the existing channel(s) you would like to change.

## Slide 44
Changing the Gas/Range Input Settings (cont’d)
Press Change Gas/Range.

## Slide 45
Changing the Gas/Range Input Settings (cont’d)
Press the parameter you want to change.
Press the current value for the parameter you want to change.
Select or type in the desired setting and press Enter.

## Slide 46
Changing the Gas/Range Input Settings (cont’d)
If you don’t see the gas and/or range you are looking for, perform the following steps:
  Press Custom+ at the top of the Input Menu

## Slide 47
Changing the Gas/Range Input Settings (cont’d)
The Custom Gas/Range menu appears:
  Press Type and select the transmitter type, then press Enter.
  Press Gas and select the gas, then press Enter. If the desired gas name is not listed, press Custom, type in a gas name, and press Enter. The gas name has a 20-character limit.
  Select the units and press Enter. If the desired units are not listed, press Custom, type in the units, and press Enter. This parameter has a 6-character limit.
  Type in the range and press Enter.
  Select a decimal point format and press Enter.
  Press Enter to return to the gas/range selection screen. The new custom gas/range will be highlighted.
  Press Enter to return to the Input Menu.
  The dead band level, noise filter, zero follower and zero correction can also be adjusted.
  When you are finished updating parameters for the selected channel(s) press the Input Menu’s Enter button.
  Press Save Changes.
  Press the arrow in the upper left corner to return to Setup Mode.
  Press the home icon in the upper right corner to return to normal operation.

## Slide 48
Changing the Alarm Settings
While in normal operation, press Setup.
If a password is enabled for Setup Mode, use the keypad to enter the password. The default password is 1234.
A pop-up message will indicate whether the relays remain active or deactivate upon entering Setup Mode. Press OK to proceed to Setup Mode.

## Slide 49
Changing the Alarm Settings (cont’d)
Press Channel Settings.

## Slide 50
Changing the Alarm Settings (cont’d)
Press the current Alarm 1, Alarm 2, or Alarm 3 setting of an existing channel you would like to change.

## Slide 51
Changing the Alarm Settings (cont’d)
Press Change Alarm X.

## Slide 52
Changing the Alarm Settings (cont’d)
The alarm’s settings menu appears.
  Press the current setting for the the parameter you want to change.
  Select or type a new setting and press Enter.
  Press the Alarm Setting menu’s Enter button.
  Press Save Changes.
  Press the arrow in the upper left corner to return to Setup Mode.
  Press the home icon in the upper right corner to return to normal operation.

## Slide 53
Changing the Location
While in normal operation, press Setup.
If a password is enabled for Setup Mode, use the keypad to enter the password. The default password is 1234.
A pop-up message will indicate whether the relays remain active or deactivate upon entering Setup Mode. Press OK to proceed to Setup Mode.

## Slide 54
Changing the Location (cont’d)
Press Channel Settings.

## Slide 55
Changing the Location (cont’d)
Press the current location(s) for the channel(s) you would like to change

## Slide 56
Changing the Location (cont’d)
Press Change Location.
  Type in the desired location (uppercase letters, lowercase letters, numbers, and/or symbols – 20-character limit)
  Press Enter.
  Press Save Changes.
  Press the arrow in the upper left corner to return to Setup Mode.
  Press the home icon in the upper right corner to return to normal operation.

## Slide 57
Creating Custom Ranges, Gases & Units
While in normal operation, press Setup.
If a password is enabled for Setup Mode, use the keypad to enter the password. The default password is 1234.
A pop-up message will indicate whether the relays remain active or deactivate upon entering Setup Mode. Press OK to proceed to Setup Mode.

## Slide 58
Creating Custom Ranges, Gases & Units (cont’d)
Press Custom Names.

## Slide 59
To add a Custom Gas/Range:
  Press Add Gas/Range
  Select the desired detector type
  Select the desired gas
  Select the desired unit and press Enter.
  Type in the desired full scale value for the gas/range and press Enter.
  Select a decimal point format and press Enter.
    Use the format xxx0 for ranges with increments of 10 or greater
    Use the format 0.xxx for ranges with increments less than 1.0
  Press Enter in the Custom Gas/Range menu.
  The custom gas name appears under the Gas Ranges section on the screen.
Creating Custom Ranges, Gases & Units (cont’d)

## Slide 60
To add a Custom Gas
  Press Add Gas
  Type in the desired custom gas name.
  Press Enter.
  The custom gas name appears under the Custom Gases section on the screen.
Creating Custom Ranges, Gases & Units (cont’d)

## Slide 61
To add a Custom Unit
  Press Add Unit.
  Type in the desired custom gas name.
  Press Enter.
  The custom unit appears under the Custom Units section on the screen.
Creating Custom Ranges, Gases & Units (cont’d)
To DELETE a customer gas/range, custom gas, or custom unit:
  Select the gas range, gas, or unit you want to delete.
  Press Delete Gas/Range, Delete Gas, or Delete Unit.
  Press Save Changes.
Press the arrow in the upper left corner to return to Setup Mode.
Press the home icon in the upper right corner to return to normal operation.

## Slide 62
Assigning Main Relays
While in normal operation, press Setup.
If a password is enabled for Setup Mode, use the keypad to enter the password. The default password is 1234.
A pop-up message will indicate whether the relays remain active or deactivate upon entering Setup Mode. Press OK to proceed to Setup Mode.

## Slide 63
Assigning Main Relays (cont’d)
Press Main Relays

## Slide 64
Assigning Main Relays (cont’d)
Select the alarm condition(s) of the relay assignment(s) you would like to change

## Slide 65
Assigning Main Relays (cont’d)
Press Select Relays.

## Slide 66
Assigning Main Relays (cont’d)
The relay selection menu appears.
If the alarms you selected already had relay assignments, the discrepancies between those assignments will be highlighted in red. You must either select or deselect those relays before pressing Enter.
Once you have selected the relay(s) that you want assigned to the selected alarm or fail conditions, press Enter.
Change the relay allocations for any other alarm or fail conditions, if desired.
Press Save Changes.
Press the arrow in the upper left corner to return to Setup Mode.
Press the home icon in the upper right corner to return to normal operation.

## Slide 67
Assigning Card Relays
While in normal operation, press Setup.
If a password is enabled for Setup Mode, use the keypad to enter the password. The default password is 1234.
A pop-up message will indicate whether the relays remain active or deactivate upon entering Setup Mode. Press OK to proceed to Setup Mode.

## Slide 68
Assigning Card Relays (cont’d)
Press Card Relays

## Slide 69
Assigning Card Relays (cont’d)
Select the alarm condition(s) of the relay assignment(s) you would like to change.

## Slide 70
Assigning Card Relays (cont’d)
Press Select Relays.

## Slide 71
Assigning Card Relays (cont’d)
The relay selection screen appears:
  Once you have selected the relay(s) that you want assigned to the selected alarm or fail conditions, press Enter.
  Press Save Changes.
  Press the arrow in the upper left corner to return to Setup Mode.
  Press the home icon in the upper right corner to return to normal operation.
NOTE
  Squares with a gray background are not installed relays and cannot be assigned. Blue or white squares are installed relays that can be assigned.
  If the alarms you selected already had relay assignments, those relay assignments will be highlighted red. You must either select (BLUE) or deselect (WHITE) those relays before pressing Enter.

## Slide 72
Calibration Mode
Fresh Air Adjust | This operation allows you to set the fresh air reading of the selected channel(s) to zero (20.9% for an oxygen channel).
Gas Adjust | This operation allows you to set the response reading of the selected channels with calibration gas.
Min/Max Spans | This operation gives a measure of how much gas response adjustment remains on a direct connect type channel by allowing you to view the minimum and maximum possible adjustment on gas during the most recent calibration for each channel.
Set Timeout | This operation controls the amount of time (5 to 240 minutes) that has to pass before the Beacon 3200 will time out of Calibration Mode.
Install Dates | This parameter displays the install and calibration dates. Both of these fields can be updated manually. • The Install Date field is populated when a channel is added and updated if the channel's head type or gas/ range is changed. • The Calibration Date field is populated when exiting Calibration Mode after performing a complete calibration (fresh air adjust and gas adjust).

## Slide 73
Calibration Mode (cont’d)
Performing a Fresh Air Adjustment
While in normal operation, press Calibrate.
If a password is enabled for Calibration Mode, use the keypad to enter the password. The default password is 1234.
NOTE:
  A pop-up message will indicate whether the selected channel relays remain active or deactivate upon entering Calibration Mode. Press OK to proceed to Calibration Mode.

## Slide 74
Calibration Mode (cont’d)
Performing a Fresh Air Adjustment
Press Gas Adjust.

## Slide 75
Calibration Mode (cont’d)
Performing a Fresh Air Adjustment
Select the desired channel(s) you for fresh air adjustment by pressing anywhere on a channel’s line. You can select all channels by pressing Select All.

## Slide 76
Calibration Mode (cont’d)
Performing a Fresh Air Adjustment
Direct Connect Channels | 4-20 mA type Detector Heads | Direct Connect heads NOT in a fresh air environment
Apply zero air if needed | Calibrate at head | Apply zero air to each selected detector for two minutes

## Slide 77
Calibration Mode (cont’d)
Performing a Fresh Air Adjustment
Press Fresh Air Adjust.
The Beacon 3200 will perform a fresh air adjustment and the display indicates Passed for each direct connect type detector head if the air adjust is successful.
If the air adjust is not successful for any channel, the display indicates FAIL for that channel and shows why.
Press the arrow in the upper left corner screen to return to the Calibration Mode Menu.
Press the home icon in the upper right corner to return to normal operation.

## Slide 78
Performing a Gas Adjustment
While in normal operation, select the desired channel(s) for fresh air adjustment by pressing anywhere on a channel’s line.
Press Calibrate.
If a password is enabled for Calibration Mode, use the keypad to enter the password. The default password is 1234.
Calibration Mode (cont’d)

## Slide 79
Performing a Gas Adjustment
Press Gas Adjust.
Calibration Mode (cont’d)

## Slide 80
Performing a Gas Adjustment
Select the channel(s) you want to calibrate by pressing anywhere on that channel(s) line. You can select all channels by pressing Select All.
Calibration Mode (cont’d)

## Slide 81
Performing a Gas Adjustment
Direct Connect Channels | 4-20 mA type Detector Heads
Apply Gas | Calibrate at head
Calibration Mode (cont’d)

## Slide 82
Performing a Gas Adjustment
To adjust the auto cal value:
  Press the value you want to change and then press Change Autocal.
  Type in the autocal value using the keypad and press Enter. Be sure the auto cal value matches the concentration listed on the calibration cylinder.
  If you change the auto cal value from its default value, the text turns red. This does not mean that the auto cal value is incorrect. It just means that it differs from the default setting.
Calibration Mode (cont’d)

## Slide 83
Performing a Gas Adjustment
Press Gas Adjust.
  The Beacon 3200 performs a gas adjustment and the display indicates Passed for each direct connect type detector head if the gas adjustment is successful. If the gas adjustment is not successful for any channel, the display indicates FAIL for that channel and shows why.
Press the arrow in the upper left corner of the screen to return to Calibration Menu.
Press the home icon in the upper right corner to return to normal operation.
NOTE:
  Allow time for the calibration gas to clear from the detector(s).
Calibration Mode (cont’d)

## Slide 84
Viewing Minimum/Maximum Spans
This operation allows you to see how much gas response adjustment remains on direct connect type channels after a calibration is performed. This is a useful gauge for whether or not a sensor is nearing the end of its life. The minimum and maximum span values are only generated for direct connect type channels. For 4 - 20 mA transmitter type channels, the Minimum Span and Maximum Span columns will be blank.
While in normal operation, press Calibrate.
If a password is enabled for Calibration Mode, use the keypad to enter the password. The default password is 1234.

## Slide 85
Viewing Minimum/Maximum Spans (cont’d)
Press Calibrate.
If a password is enabled for Calibration Mode, use the keypad to enter the password. The default password is 1234.

## Slide 86
Viewing Minimum/Maximum Spans (cont’d)
Press View Min/Max Spans.

## Slide 87
Viewing Minimum/Maximum Spans (cont’d)
The minimum and maximum span for each channel will be displayed, if available and appropriate. 4-20 mA detector heads will not have a minimum or maximum span displayed.
Press the arrow in the upper left corner of the screen to return to Calibration Mode Menu.
Press the home icon in the upper right corner to return to normal operation.

## Slide 88
Setting the Timeout
While in normal operation, press Calibrate.
If a password is enabled for Calibration Mode, use the keypad to enter the password. The default password is 1234.

## Slide 89
Setting the Timeout
While in normal operation, press Calibrate.
If a password is enabled for Calibration Mode, use the keypad to enter the password. The default password is 1234.

## Slide 90
Setting the Timeout (cont’d)
Press Change Timeout.

## Slide 91
Setting the Timeout (cont’d)
A number pad appears. Type in a new value (1-240 minutes).
Press Enter to save the parameter.
Press the arrow icon in the upper left corner of the screen or the home icon in the upper right corner of the screen to return to normal operation.

## Slide 92
Changing the Install & Calibration Dates
While in normal operation, press Calibrate.
If a password is enabled for Calibration Mode, use the keypad to enter the password. The default password is 1234.
Each Channel’s sensor installation and calibration dates are updated automatically but can also be changed manually.
Installation Date: The installation date is automatically saved when a channel is created and is updated when the channel’s head type or gas/range are changed.
Calibration Date: The calibration date is automatically saved when exiting Calibration Mode after performing a complete calibration (fresh air adjust and gas adjust)

## Slide 93
Changing the Install & Calibration Dates (cont’d)
Press Install Dates.

## Slide 94
Changing the Install & Calibration Dates (cont’d)
The install date and calibration date will be displayed for each channel.

## Slide 95
Changing the Install & Calibration Dates (cont’d)
To change the install date or calibration date for one or more channels, select the dates you want to change. Multiple dates or multiple calibration dates can be changed at once, but both cannot be changed at the same time.

## Slide 96
Changing the Install & Calibration Dates (cont’d)
Press Change Date.
A number pad appears with the current time and date automatically filled in. Select the year, month, date, hour, minute, and second.
Press Enter. Change more dates, if necessary.
Press Save Changes.
Press the arrow in the upper left corner of the screen to return to the Calibration Mode Menu.
Press the arrow in the upper right corner to return to normal operation.

## Slide 97
Maintenance
While in normal operation, press Calibrate.
If a password is enabled for Calibration Mode, use the keypad to enter the password. The default password is 1234.
Alarm Test
Preventive maintenance of the Beacon 3200 and its detector heads consists of daily, monthly, and quarterly procedures to ensure that the installed detector heads remain on zero (20.9 for oxygen) in fresh air and are responsive to the target gas.

## Slide 98
Maintenance (cont’d)
While in normal operation, press Setup.
If a password is enabled for Setup Mode, use the keypad to enter the password. The default password is 1234.
A pop-up message will indicate
Alarm Test

## Slide 99
Maintenance (cont’d)
Press Alarm Test.
Alarm Test

## Slide 100
Maintenance (cont’d)
Press Alarm Test screen appears, displaying up to 16 configured channels and row of buttons.
Alarm Test

## Slide 101
Maintenance (cont’d)
The following list describes the function of each button and their effect on the relays of selected channels.
Alarm Test
Alarm 1:
Pressing the Alarm 1 button will ramp the reading for any selected channel(s) and the 4-20 mA output up (or down if Alarm 1 is a decreasing alarm for an oxygen channel) until it reaches the Alarm 1 setpoint.
All Alarm 1 indications will be initiated and any relays mapped to the Alarm 1 condition for the selected channel(s) will activate (or deactivate if defined as NE).

## Slide 102
Maintenance (cont’d)
Alarm Test
Alarm 2:
Pressing the Alarm 2 button will ramp the reading for any selected channel(s) and the 4-20 mA output up (or down if Alarm 2 is a decreasing alarm for an oxygen channel) until it reaches the Alarm 2 setpoint.
All Alarm 2 indications will be initiated and any relays mapped to the Alarm 2 condition for the selected channel(s) will activate (or deactivate if defined as NE).

## Slide 103
Maintenance (cont’d)
Alarm Test
Alarm 3:
Pressing the Alarm 3 button will ramp the reading for any selected channel(s) and the 4-20 mA output up (or down if Alarm 3 is a decreasing alarm for an oxygen channel) until it reaches the Alarm 3 setpoint.
All Alarm 3 indications will be initiated and any relays mapped to the Alarm 3 condition for the selected channel(s) will activate (or deactivate if defined as NE).

## Slide 104
Maintenance (cont’d)
Alarm Test
Page Up & Page Down:
Pressing Page Up or Page Down buttons will scroll between the first and second screen of all configured channels.

## Slide 105
Maintenance (cont’d)
Alarm Test
Cancel Test:
Pressing the Cancel Test button returns the reading(s) and 4-20 mA output(s) to their fresh air values and deactivates all relays associated with the alarms triggered during the test.

## Slide 106
Maintenance (cont’d)
Alarm Test
Back Arrow:
Pressing the back arrow button navigates back to the Setup Mode screen.

## Slide 107
Maintenance (cont’d)
Alarm Test
Reset/Clear:
Pressing the Reset/Clear button clears any alarm conditions that have passed and deactivates any relays associated with those alarm conditions.
For example, if Alarm 1 is pressed after Alarm 3, the Alarm 2 and Alarm 3 conditions will persist for the selected channel(s) even though the reading(s) have changed to the Alarm 1 setpoint(s). Pressing the Reset/Clear button will clear Alarm 2 and Alarm 3 on the selected channel(s) and deactivate any relays associated with those alarm conditions.

## Slide 108
Sensor Logs Program
Plug a USB drive into the connector at the bottom of the display’s PCB’s right edge.
While in normal operation, press Setup.
If a password is enabled for Setup Mode, use the keypad to enter the password. The default password is 1234.
When a data file is saved to a USB drive, the Beacon 3200 generates the file name using the current date. Multiple .RKI files saved to the same location on the same day will have identical file names. Data files should be renamed before saving additional logs on the same day.
Saving Logged Data to a USB Drive

## Slide 109
Sensor Logs Program (cont’d)
Press Save Logs.
Saving Logged Data to a USB Drive

## Slide 110
Sensor Logs Program (cont’d)
A progress bar tracks the data-writing status.
The Cancel button changes to a Done button when the data-writing is finished.
Press Done.
Press the arrow in the upper left corner or the home icon in the upper right corner to return to normal operation.
Saving Logged Data to a USB Drive

## Slide 111
Sensor Logs Program (cont’d)
Saving Logged Data to a USB Drive
A data file is created on the USB drive (.RKI format). File names are assigned using the date that the file was created.

## Slide 112
Parts List
Part No. | Description
18-0020 | Housing conduit hub plug
18-0107RK | Conduit hub (3/4 NPT)
43-0440RK | Reset switch
43-4170RK | AC fuse, 6A, 250 V, 1/4 x 1 1/4 inch, fast acting
43-4179RK | DC fuse, 10A, 250V, 1/4 x 1/4 inch, fast acting
51-0001-AMB | Strobe, amber, 24 VDC, NEMA 4X
51-0001-BLU | Strobe, blue, 24 VDC, NEMA 4X
51-0001-RED | Strobe, red, 24 VDC, NEMA 4X
51-0096RK | Strobe/horn, 10 - 33 VDC, NEMA 4X
51-0170 | Strobe, amber, 12 - 48 VDC, NEMA 4X
51-0171 | Strobe, blue, 12 - 48 VDC, NEMA 4X
51-0174 | Strobe, red, 12 - 48 VDC, NEMA 4X
52-1016RK | Buzzer
57-0168-01 | Sensor module
57-0169-01 | Relay module
71-0435 | Beacon 3200 Gas Monitor Operator’s Manual (this document)
82-6110 | SD card, 32 GB
Parts List

## Slide 113
Questions?