## Slide 1: Beacon 800
Beacon 800, 8 channel gas detection system

## Slide 2: Internal Components
PCB Control Switches
ESCAPE
UP/YES
DOWN/NO
ENTER
Alarm LEDs
Alarm 1, yellow
Alarm 2, orange
Alarm 3, red
Fail, yellow
On/Off toggle switch behind display
94 dB Buzzer Alarm
Alarm Reset Switch
Backlit LCD Display
8 Channels Displayed Simultaneously
NEMA-4X weather resistant enclosure
Accepts any 4-20 mA transmitter
2 programmable alarm levels per channel

## Slide 3: Alarm Indications
Condition | Cause | Visual Indications | Audible Indications
Alarm 1 | Increasing (decreasing for O2) gas reading at or above the alarm 1 set point | Alarm 1 LED on Gas reading alternates with Alarm-1 message Strobe (if installed) activates | Steady tone
Alarm 2 | Increasing gas reading at or above the alarm 2 set point | Alarm 2 LED is on Gas readings alternates with ALARM 1 and ALARM-2 messages Strobe (if installed) activates | Steady tone
Fail | Disconnected or misconnected detector head wiring Display reading at -10% of full scale or lower Defective component | Fail LED is on Fail message replaces gas reading Strobe (if installed) activates | Steady tone
Low Power | No AC power and DC power source (primary or backup) less than 21.5 volts. | Fail LED is on SUPPLY VOLTAGE IS TOO LOW LOW POWER STANDBY message and actual voltage of incoming DC power | None

## Slide 4: Configuration Menu
Press and hold the ESCAPE and ENTER buttons to enter the Configuration Menu.

## Slide 5: Configuration Menu
Configuration Screen.
  Press the YES button to enter.
  Using the UP button, you can select from three options.

## Slide 6: Configuration Menu
Enable / Disable Channel(s)
  Press the ENTER button to enter this menu.
  This menu is used for making the selected channel ACTIVE, DISABLED or NOT USED.

## Slide 7: Configuration Menu
Select the channel that you would like to change.
Press the ENTER button.

## Slide 8: Configuration Menu
To make a channel active, set to CHANNEL ENABLED.
If not, press the DOWN/NO button to change.

## Slide 9: Configuration Menu
If you wish to disable this channel press the ENTER button.
If not, continue to press the DOWN button.

## Slide 10: Configuration Menu
When the channel is set to NOT USED, the LCD will be blank for this channel location.
When completed with selection always press the ENTER button.

## Slide 11: Configuration Menu
Enter Calibration Mode.
  Press the ENTER button to proceed.
  Locks out alarms and relay functions when in Calibration Mode.

## Slide 12: Configuration Menu
Select CALIBRATION TIMEOUT using the UP or DOWN buttons.
If monitor is left idle in this mode, after timeout period, the monitor will return to normal operation.

## Slide 13: Configuration Menu
Maximum TIMEOUT is 240 minutes.
Press the ENTER button when TIMEOUT is set.
All calibrations are done at the transmitter.
Press the ESCAPE button to exit.

## Slide 14: Configuration Menu
Configure Channel Settings
  Press the ENTER button to proceed.
  Allows setting of all parameters of each active channel.

## Slide 15: Configuration Menu
Using the UP or DOWN buttons, select the channel that you want to configure then press the ENTER button.

## Slide 16: Configuration Menu
Select UNITS and GAS TYPE
Press YES or NO
Change as required then press the ENTER button.

## Slide 17: Configuration Menu
ALARM-1 Level
Press YES if okay, NO if change is required.
Use UP or DOWN buttons to change to desired value, then press ENTER.

## Slide 18: Configuration Menu
Press YES if okay.
Press NO to select.
  0-15 seconds 1 second increments.
  15 seconds to 1 minute in 30 second increments.
  1 minute to 10 minutes in 1 minute increments.
  10 minute to 60 minutes in 10 minute increments.
  Factory default is 1 seconds.

## Slide 19: Configuration Menu
ALARM-1 OFF DELAY
Press the YES button if okay, NO if adjustment is required.
Use UP or DOWN buttons to set to desired level.
Factory default is 0 seconds.

## Slide 20: Configuration Menu
Alarm-1 Increasing
If okay press YES, if not, press the NO button.
DECREASING will be displayed
Press ENTER when completed.

## Slide 21: Configuration Menu
Press the YES button if okay.
If not, press the NO button and NORMALLY ENERGIZED will be displayed.
Press ENTER when done.

## Slide 22: Configuration Menu
Press the YES button if okay.
Press the NO button and SELF-RESETTING will be displayed.
Press the ENTER button to set.

## Slide 23: Configuration Menu
Press the YES button to accept this setting.
Press the NO button to change.
Press ENTER button when completed.

## Slide 24: Configuration Menu
ALARM-2 Level
Press YES if okay, NO if change is required.
Use UP or DOWN buttons to change to desired value.

## Slide 25: Configuration Menu
Press YES if okay.
Press NO to select.
  0-15 seconds 1 second increments.
  15 seconds, 30 seconds to 1 minute
  1 minute to 10 minutes in 1 minute increments.
  10 minutes to 60 minutes in 10 minute increments.
  Factory default is 1 second.

## Slide 26: Configuration Menu
ALARM-2 OFF DELAY
Press the YES button if okay, NO if adjustment is required.
Use the UP or DOWN buttons to set to desired level.
Factory default is 0 seconds.

## Slide 27: Configuration Menu
Alarm-2 Increasing
If okay press YES, if not, press the NO button.
DECREASING will be displayed
Press ENTER when completed.

## Slide 28: Configuration Menu
Press the YES button if okay. If not, press the NO button.
NORMALLY ENERGIZED will be displayed.
Press ENTER when done.

## Slide 29: Configuration Menu
Press the YES button if okay.
Press the NO button and SELF-RESETTING will be displayed.
Press the ENTER button to set.

## Slide 30: Configuration Menu
Noise filter can be adjusted to minimize display instability.

## Slide 31: Configuration Menu
ZERO SUPPRESSION is used to minimize small deviations from zero.
For LEL, 2% of Full Scale is the factory default.
In this case, +/- 2% LEL would read zero on the display.

## Slide 32: Configuration Menu
When completed, press the YES button to save all changes made.
Select other channels if change to configuration is required.

## Slide 33: Accessing Connections
Loosen thumb screws.
Swing display to the left to allow entry inside.

## Slide 34: Accessing Connections
Display on hinges allows easy access to internal components and wiring connections.

## Slide 35: Accessing Connections
On/Off switch
Fuses
Power, Transmitter and Relay connections are easily accessed.

## Slide 36: Relay Wiring
Make sure that devices that are controlled by relays do not exceed the rating of the relay.
Improper wiring of relays can destroy the relay and circuit board.

## Slide 37: Questions?